Selection Manual of SRE Series Card IO

Content

EtherCAT Communication Coupler	3

Digital Input Module	4

Digital Output Module	6

Digital I/O Terminal	8

Analog Input Module	10

Analog Fast Acquisition Input Module	12

RTD Measurement Module	14

Thermocouple Measurement Module	16

Analog Output Module	18

Serial Port Module	20

CAN Protocol Conversion Module	21

PROFINET Protocol Conversion Module	22

DeviceNet Protocol Conversion Module	23

Profibus DP Protocol Conversion Module	24

High-speed Counting Module	25

Pulse Output Module	27

Digital Fast Output Module	28

Power Relay Module	29

EtherCAT Communication Coupler

Product Features

● 2 RJ45 communication ports (IN, OUT)

● The backplane bus can be directly expanded with 64 expansion modules

Product Specifications

| Technical specifications |  |
| --- | --- |
| Electrical interfaces | RJ45 |
| Power supply input/output power supply | 24VDC (rated), output current < 10A |
| Operating current consumption | 188mA |
| Number of expansion modules | Expands with 64 modules |
| Bus +5VDC current capacity | <2A (If the number of expansion modules exceeds 8, be sure to add a power relay module) |
| Support protocols | EtherCAT slaves |
| Slave settings |  |
| Address settings | Master assignment |
| Maximum number of stations per segment | 255 |
| Isolation |  |
| Between the channel and the bus | Yes |
| Power to bus | Yes |
| The body comes with the number of IO | NA |
| Display instructions | Power supply +24V green light, BF red light, SF red light, NET red light |
| Diagnosis and alarm of system power supply | Support |
| Working environment | Operating ambient temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |
| Dimension(L×W×H) | 50*100*70 |

Ordering data

| Specification | Order No. |
| --- | --- |
| High performance EtherCAT coupler, 2 RJ45 ports, EtherCAT backplane bus, can directly expand to 64 IO terminals, 24VDC power supply | SRE8200 |

Digital Input Module

Product  Features

● Input photoelectric isolation

● Filter can be configured

● Bus and channel isolation technology, reliable

● 150us fast response

Product Specifications

| Technical specifications |  |  |  |
| --- | --- | --- | --- |
| Order No. | SRE1016 | SRE1032 |  |
| Input points | 16 | 32 |  |
| Bus 5VDC current consumption | ＜50mA | 210mA | 117mA |
| Cable length (shielded) | Maximum 500m |  |  |
| Cable length (unshielded) | Maximum 300m |  |  |
| Input voltage |  |  |  |
| ● Rated value | 24VDC |  |  |
| ● “0” signal | Maximum 5VDC,1mA |  |  |
| ● “1” signal | Minimum 15VDC,2.5mA |  |  |
| Input delay |  |  |  |
| ● From 0 to 1, minimum | 150us | 300us |  |
| ● From 1 to 0, minimum | 150us | 300us |  |
| Input properties | Source/Leakage | Source/Leakage |  |
| Allowable static current | 1mA |  |  |
| Insulation | 500VDC |  |  |
| Isolation |  |  |  |
| ●Between channel and bus | Yes |  |  |
| ●Between channels | Yes |  |  |
| Display indication | Green LED display for each channel input |  |  |
| Diagnosis and alarm of system power supply | Support |  |  |
| Operating environment | Operating ambient temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |  |  |
| Dimension(L×W×H) | 12*100*80 | 24*100*80 |  |

Ordering data

| Specification | Order No. |
| --- | --- |
| Digital input module, 16 inputs, support PNP/NPN input, 24VDC, module diagnostic function, SRE8200 can expand to 64 modules. | SRE1016 |
| Digital input module, 32 inputs, support PNP/NPN input, 24VDC, module diagnostic function, SRE8200 can expand 64 to modules. | SRE1032 |

Digital Output Module

Product  Features

● Output photoelectric isolation

●Overvoltage and short circuit protection functions

● Bus and channel isolation technology, reliable

● 150us fast response

Product  Specifications

| Technical specifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| Order No. | SRE2216 | SRE2116 | SRE2232 | SRE2132 |
| Output type | PNP-type solid-state MOSFETs | NPN-type solid-state MOSFETs | PNP-type solid-state MOSFETs | NPN-type solid-state MOSFETs |
| Output points | 16 |  | 32 |  |
| Bus 5VDC current consumption | ＜50mA |  | 210mA | 186mA |
| Cable length (shielded) | Maximum 500m |  |  |  |
| Cable length (unshielded) | Maximum 150m |  |  |  |
| Output short circuit protection | Yes , electronic |  |  |  |
| Leakage current | ＜1mA |  |  |  |
| Maximum lamp load | 5W |  |  |  |
| Output current “1” | 0.5A |  |  |  |
| Overcurrent protection threshold | 1.5A,5ms |  |  |  |
| Contact mechanical life | -- |  |  |  |
| Contact electrical life (rated load) | -- |  |  |  |
| Switch frequency |  |  |  |  |
| ●Resistive load, maximum | 1KHZ |  |  |  |
| ●Inductive load, maximum | 0.5HZ |  |  |  |
| ●Lamp load, maximum | 10HZ |  |  |  |
| ●Mechanical load, maximum | -- |  |  |  |
| Insulation test voltage | 500VDC |  |  |  |
| Isolation |  |  |  |  |
| ●Between the channel and the bus | Yes |  |  |  |
| ●Between channels | Yes |  |  |  |
| Display instructions | Each channel output green LED display |  |  |  |
| Diagnosis and alarm of system power supply | Support |  |  |  |
| Operating environment | Operating temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |  |  |  |
| Dimension(L×W×H) | 12*100*80 |  | 24*100*80 |  |

Ordering data

| Specification | Order No. |
| --- | --- |
| Digital output module, 16 outputs, transistor PNP type, rated 24VDC/0.5A, module diagnostic function, SRE8200 can expand to 64 modules. | SRE2116 |
| Digital output module, 32 outputs, transistor PNP type, rated 24VDC/0.5A, the total of a single module does not exceed 10A, the module diagnostic function, SRE8200 can expand to 64 modules. | SRE2132 |
| Digital output module, 16 outputs, transistor NPN type, rated 0VDC (±3V)/0.5A, module diagnostic function, SRE8200 can expand to 64 modules. | SRE2016 |
| Digital output module, 32 outputs, transistor NPN type, rated 0VDC (±3V)/0.5A, the total of a single module does not exceed 10A, module diagnostic function,SRE8200 can expand to 64 modules. | SRE2032 |

Digital I/O Terminal

Product Features

● Input two-way photoelectric isolation

● Reverse polarity protection function

●Overvoltage and overcurrent protection functions

● Bus and channel isolation technology

● Compatible design, easy to apply

Product Specifications

| Technical specifications |  |  |  |
| --- | --- | --- | --- |
| Order No. | SRE1432 |  | SRE1332 |
| Product overview | 16-point PNP input 16-point transistor PNP type output |  | 16-point NPN input 16-point transistor NPN type output |
| Input characteristics |  |  |  |
| Input points | 16 |  |  |
| Input voltage |  |  |  |
| ●Rated voltage | 24VDC |  |  |
| ● “0” signal | Maximum 5VDC,1mA |  |  |
| ● “1” signal | Minimum 15VDC,2.5mA |  |  |
| Input delay |  |  |  |
| ● From 0 to 1, minimum | 1.2~4.8ms |  |  |
| ● From 1 to 0, minimum | 1.2~4.8ms |  |  |
| Input characteristics | Source |  | Leakage |
| Output type | Solid state MOSFET |  |  |
| Output points | 16 |  |  |
| Output cable length (shielded) | Maximum 500m |  |  |
| Output cable length (unshielded) | The longest input point is 300m, and the longest output point is 150m |  |  |
| Output short circuit protection | Yes, electronic |  |  |
| Maximum lamp load | 5W |  |  |
| Output current “1” | 0.5A |  |  |
| Overcurrent protection threshold | 1.5A,5ms |  |  |
| Switch frequency |  |  |  |
| Resistive load, maximum | 100HZ |  |  |
| Inductive load, maximum | 0.5HZ |  |  |
| Lamp load, maximum | 10HZ |  |  |
| Mechanical load, maximum | -- |  |  |
| Insulation test voltage | 500VDC |  |  |
| Isolation |  |  |  |
| Between channel and bus |  | Yes |  |
| Between channels |  | Yes |  |
| Display indication |  | Green LED display for each channel output |  |
| Operating environment |  | Operating ambient temperature: -20～60℃, Relative humidity: 5%～90% (no condensation) |  |
| Dimension(L×W×H) |  | 24*100*80 |  |

Ordering data

| Specification | Order No. |
| --- | --- |
| Digital I/O module, 16-point PNP input, 16-point transistor PNP output, module diagnostic function | SRE1432 |
| Digital I/O module, 16-point NPN input, 16-point transistor NPN output, module diagnostic function | SRE1332 |

Analog Input Module

Product Features

● Configure the range through  XML file, more flexible to use

● Reliable bus isolation technology

● 1ms fast response

● Channel update time can be configured

Product Specifications

| Technical specifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| Order No. |  | SRE3204 | SRE3208 |  |
| Input points |  | 4 Inputs, Voltage/Current, 1ms Fast Response (Single Channel) | 8 Inputs, Voltage/Current, 1ms Fast Response (Single Channel) |  |
| Input type |  | Differential input |  |  |
| Bus 5VDC current consumption |  | 150mA |  |  |
| Cable length (shielded twisted pair) |  | Maximum 100m |  |  |
| Power supply polarity protection |  | Support |  |  |
| Output voltage |  | 10VDC, Maximum output current 300mA, used for electronic ruler power supply |  |  |
| Maximum sustainable voltage |  | 30VDC |  |  |
| Measuring range |  |  |  |  |
| Voltage (Unipolar) |  | 0~10V |  |  |
| Voltage (Bipolar) |  | / |  |  |
| Current |  | 0~20mA |  |  |
| Data word |  |  |  |  |
| Unipolar |  | 0~32000,Full scale |  |  |
| Bipolar |  | / |  |  |
| Resolution |  |  |  |  |
| Voltage (unipolar) |  | 16-bit |  |  |
| Voltage (bipolar) |  | / |  |  |
| Current |  | 15 bit |  |  |
| Analog-to-digital conversion time |  | Less than 300us |  |  |
| Simulates input step response |  | 1ms to 95% |  |  |
| Common mode rejection |  | 40dB,DC-60HZ |  |  |
| Common-mode voltage |  | Signal voltage + common mode voltage (within +12V) |  |  |
| Input impedance |  | ≥10MΩ (at voltage input) |  |  |
| Isolation |  |  |  |  |
| Between channel and bus | Yes |  |  |  |
| Display indication | Power supply green LED display |  |  |  |
| System power diagnostics and warnings | Support |  |  |  |
| Operating environment | Working ambient temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |  |  |  |
| Dimension(L×W×H) | 12*100*80 |  |  | 24*100*80 |

Ordering data

| Specification | Order No. |
| --- | --- |
| Analog input module, 16-bit accuracy, 4-channel voltage/current input, module diagnostic function, SRE8200 can expand to 64 modules. | SRE3204 |
| Analog input module, 16-bit accuracy, 8-channel voltage/current input, module diagnostic function, SRE8200 can expand to 64 modules. | SRE3208 |

Analog Fast Acquisition Input Module

Product Features

● Configure the range through XML files, more flexible to use

● Reliable bus isolation technology

● Channel update time can be configured

Product Specifications

| Ordering data |  |
| --- | --- |
| Model | 2-channel fast acquisition module |
| Product overview | Two-channel analog fast acquisition module |
| Technical specifications |  |
| Supply voltage | 18~28V DC |
| Number of input channels | 2 |
| Acquisition type | Voltage |
| Measuring range |  |
| Voltage | -10V-10V |
| Data word |  |
| Bipolar | -32000~32000 |
| Resolution | 16-bit |
| Input type | Differential input |
| Sampling type | At the same time |
| Oversampling coefficient | n = 1...100 optional (maximum 100 ksamples/s) |
| Maximum sampling rate | Maximum 10 µs/100 ksps (per channel, synchronization) |
| Isolation |  |
| Between the channel and the bus | Yes |
| Display instructions | Power supply green LED display |
| Distributed cock | Support |
| Diagnosis and alarm of system power supply | Support |
| Operating environment |  |
| Operating temperature | Working ambient temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |
| Vibration/shock resistance | Comply with EN 60068-2-6/EN 60068-2-27 standard |
| Anti-EMI/anti-EMI performance | Comply with EN 61000-6-2/EN 61000-6-4 standard |
| Dimension(L×W×H) | 12×80×100 mm |

Ordering data

| Specification | Order No. |
| --- | --- |
| Analog fast acquisition input module, 16-bit accuracy, 2-channel voltage input, module diagnostic function, SRE8200 can expand to 64 modules. | SRE3522 |

RTD Measurement Module

Product Features

● Configure the type through XML files

● Advanced filtering algorithm, more stable sampling

● Reliable bus isolation technology

Product Specifications

| Technical specifications |  |
| --- | --- |
| Input points | 4 |
| Input type | RTD |
| Bus 5VDC current consumption (at full load) | 60mA |
| Supply polarity protection | Support |
| Maximum sustainable voltage | 30VDC |
| Input range | RTD type (choose anyone)：Pt-100Ω,200Ω,500Ω,1000Ω ( α=3850PPM,3920PPM, 3850.55PPM,3916PPM,3902PM) ;Pt-10000Ω ( α=3850PPM) ; Cu-9.035Ω ( α=4720PPM); Ni- 10Ω,120Ω,1000Ω ( α=6720PPM,6178PPM);R-150,300Ω,600Ω |
| Measuring principle | Sigma-Delta |
| Data word | -27648~+27648 |
| Resolution |  |
| Temperature | 0.1℃/0.1℉ |
| Resistance | 15 bit + symbol bit |
| Measurement transition time | < 400ms |
| Common mode rejection | >125dB, AC120V |
| Cable length (compensating wire) | Up to 30m long |
| Lead wire loop resistance | Maximum 100Ω |
| Input impedance | ≥ 1MΩ |
| Basic error | ≤ 0.1%FS |
| Consistency | 0.05%FS |
| Cold end error | -- |
| Isolation |  |
| Between channel and bus | Yes |
| Between power supply and bus | Yes |
| Between channel and power supply | Yes |
| Display indication | Power supply green LED display |
| Diagnosis and alarm of system power supply | Support |
| Operating environment | Operating temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |
| Dimension(L×W×H) | 12×80×100 mm |

Ordering data

| Specification | Order No. |
| --- | --- |
| SRE3274 RTD measurement module, 4 inputs, 16 bit accuracy, PT100, PT1000, etc., module diagnostic function | SRE3274 |

Thermocouple Measurement Module

Product Features

● Configure the type through XML files

● Advanced filtering algorithm, more stable sampling

● Bus isolation technology and reliability

Product Specifications

| Technical specifications |  |
| --- | --- |
| Input points | 4 |
| Input type | Thermocouple |
| Bus 5VDC current consumption (at full load) | 52mA |
| Supply polarity protection | Support |
| Maximum sustainable voltage | 30VDC |
| Input range | Thermocouple type (optional): S/T/R/E/N/K/J; Voltage range: ±80mV |
| Measuring principle | Sigma-Delta |
| Data word | -- |
| Resolution |  |
| Temperature | 0.1℃/0.1℉ |
| Voltage | 15 bit + sign bit |
| Resistance | -- |
| Measurement conversion time | <400ms |
| Common mode rejection | 85dB,DC-50HZ/60HZ/400HZ |
| Cable length (compensation wire) | Maximum 30m |
| Wire loop resistance | Maximum 20Ω |
| Input impedance | ≥10MΩ |
| Basic error | ≤0.1%FS |
| Conformance | 0.05%FS |
| Cold junction error | ±1.5℃ |
| Isolation |  |
| Between channel and bus | Yes |
| Between power supply and bus | Yes |
| Between channel and power supply | Yes |
| Display indication | Power supply green LED display |
| Diagnosis and alarm of system power supply | Support |
| Operating environment | Operating temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |
| Dimension(L×W×H) | 12×80×100 mm |

Ordering data

| Specification | Order No. |
| --- | --- |
| SRE3284 thermocouple measurement module, 4 inputs, 16 bit accuracy, J, K, etc., module diagnostic function, resolution 0.1℃/0.1 ℉ | SRE3284 |

Analog Output Module

Product Features

● Overvoltage and overcurrent output protection function

● Reliable bus isolation technology

● Fast response at ms level

● Channel update time can be configured

Product Specifications

| Technical specifications |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Order No. |  | SRE4204 |  | SRE4208 |  |
| Output points |  | 4 |  | 8 |  |
| Output type |  | Voltage, current, 1.8ms fast response (single channel) |  |  |  |
| Bus 5VDC current consumption |  | 150mA |  |  |  |
| Cable length (shielded twisted pair) |  | Maximum 100m |  |  |  |
| Power supply polarity protection |  | Support |  |  |  |
| Maximum sustainable voltage |  | 30VDC |  |  |  |
| Measuring range |  |  |  |  |  |
| Voltage (unipolar) |  | 0~10V |  |  |  |
| Voltage (bipolar) |  | ±10V |  |  |  |
| Current |  | 0~20mA |  |  |  |
| Data word |  |  |  |  |  |
| Voltage |  | -32000~32000,Full scale |  |  |  |
| Current(0~20mA) |  | 0~32000 |  |  |  |
| Resolution |  |  |  |  |  |
| Voltage |  | 16 bits |  |  |  |
| Current |  | 16 bits |  |  |  |
| Analog-to-digital conversion time |  | < 300us |  |  |  |
| Analog voltage output step response |  | 0.2ms to 95% |  |  |  |
| Analog current output step response |  | 1.2ms to 95% |  |  |  |
| Output error |  | Usually ±0.5%, maximum ±2% |  |  |  |
| Common mode voltage |  | Signal voltage + common mode voltage (within +12V) |  |  |  |
| Output load |  | Voltage output: 5000Ω (minimum) Current output: 500Ω (maximum) |  |  |  |
| Isolation |  |  |  |  |  |
| ●Between channel and bus |  | Yes |  |  |  |
| Display indication |  | Power Supply Green LED Display |  |  |  |
| System power diagnostics and warnings |  | Support |  |  |  |
| Operating environment |  | Operating temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |  |  |  |
| Dimension(L×W×H) |  | 12*100*80 |  | 24*100*80 |  |

Ordering data

| Specification | Order No. |
| --- | --- |
| Analog output module, 4-channel voltage or current, ±10V or 0-20mA, module diagnostics, 16-bit accuracy.The SRE8200 can expand to 64 modules. | SRE4204 |
| Analog output module, 8-channel voltage or current, ±10V or 0-20mA, module diagnostics, 16-bit accuracy. The SRE8200 can expand to 64 modules. | SRE4208 |

Serial Port Module

Product Features

● 2/4 RS422/RS232/RS485 interfaces

● Support Modbus-RTU and free port protocol

● The fastest baud rate is 115.2KBPS, stable and reliable

● Configure the serial port parameters through XML files, the master station does not need to be programmed, and it is easy to use

Product Specifications

| Technical specifications |  |  |
| --- | --- | --- |
| Order No. | SRE6002 | SRE6004 |
| Interfaces | 2 RS422/RS232/RS485 | 4 RS422/RS232/RS485 |
| Serial support protocol | Modbus-RTU Master, slave, free port mode |  |
| Data transfer rate | 1200bps, 2400bps, 4800bps, 9.6Kbps, 19.2Kbps, 38.4Kbps, 57.6Kbps, 115.2Kbps |  |
| Check bit | No parity, odd parity, even parity |  |
| Stop bit | 1, 2 |  |
| Data bit | 7, 8 |  |
| Bus 5VDC consumption current | ＜70mA |  |
| Cable length (shielded twisted pair) | 1000m (depending on the actual baud rate used) |  |
| Distributed cock | Not Supported |  |
| Isolation |  |  |
| Between channel and bus | Yes |  |
| Display indication | Power supply green LED display |  |
| Diagnosis and alarm of system power supply | Support |  |
| Operating environment | Operating temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |  |
| Dimension(L×W×H) | 12*100*80 | 24*100*80 |

Ordering data

| Specification | Order No. |
| --- | --- |
| Serial communication module, 2 RS422/RS232/RS485 ports, support Modbus RTU and free port protocol, baud rate up to 115.2Kbps, SRE8200 can expand to 64 modules, configure serial port parameters through XML file, need not program master station, easy to use. | SRE6002 |
| Serial communication module, 4 RS422/RS232/RS485 ports, support Modbus RTU and free port protocol, baud rate up to 115.2Kbps, SRE8200 can expand to 64 modules, configure serial port parameters through XML file, need not program master station, easy to use | SRE6004 |

CAN Protocol Conversion Module

Product Specifications

| Technical specifications |  |  |
| --- | --- | --- |
| Order No. | SRE6051 | SRE6051F |
| Interface | 1 CAN interface |  |
| Support protocols | CANopen | CAN2.0A/B |
| Data transfer rate | 10kbit/s - 1Mbit/s |  |
| SDO | The maximum uplink/downlink is 512 bytes | / |
| Maximum number of CAN packets | / | 256 articles |
| Matching resistors | 120 ohms (DIP switch) |  |
| ESI file | default |  |
| Sync mode | Free to run |  |
| Network cycle time | As low as 100 μ s |  |
| Isolation |  |  |
| Between channel and bus | Yes |  |
| Display indication | Power supply green LED display |  |
| Diagnosis and alarm of system power supply | Support |  |
| Operating environment | Operating temperature: -20~60℃ , Relative humidity: 5%~90% (no condensation) |  |
| Dimension(L×W×H) | 24*100*80 | 24*100*80 |

Ordering data

| Specification | Order No. |
| --- | --- |
| CAN protocol conversion module, 1 CAN interface, support CANopen protocol, the fastest baud rate is 1Mbit/s, SRE8200 can expand to 64 modules. | SRE6051 |
| CAN protocol conversion module, 1 CAN interface, support CAN2.0A/B protocol, the fastest baud rate is 1Mbit/s, SRE8200 can expand to 64 modules. | SRE6051F |

PROFINET Protocol Conversion Module

Product Specifications

| Technical specifications |  |
| --- | --- |
| Order No. | SRE6061 |
| PROF INET specifications | V2.3 |
| PROF INET interface | Dual Ethernet 100 Mbit/s, RJ45 plug |
| Cyclic data exchange | Support |
| Off-cycle data reading and writing | Support |
| Diagnostic data and fault reading | Support |
| Maximum number of slaves | 128 |
| Maximum data supported by a single slave | 1440bytes IN+1440bytes OUT |
| Maximum output data | 1.5Kbytes |
| Maximum input data | 1.5Kbytes |
| PN slave single polling cycle | Can be set to allow different slave polling cycles, with a minimum period of 2ms |
| PN network configuration size | 512Kbytes |
| IRT | Not Supported |
| ES I file | Default |
| CoE | Support |
| Network cycle time | As low as 100 µs |
| Addressing mode | Logic, node, and location |
| Command | APRD , ARMW , APWR , BRD , BWR , FPRD , FPRW ,FPWR , FRMW , LRD , LRW , LWR |
| Synchronization mode | Free operation |
| Link Mode | Dual network port daisy chain |
| Isolation |  |
| Between channel and bus | Yes |
| Display indication | Power supply green LED display |
| Diagnosis and alarm of system power supply | Support |
| Operating environment | Operating temperature: -20~60℃ , Relative humidity: 5%~90% (no condensation) |
| Dimension(L×W×H) | 24*100*80 |

Ordering data

| Specification | Order No. |
| --- | --- |
| PROF INET protocol conversion module, PROF INET specification: V2.3, support 128 slaves. | SRE6061 |

DeviceNet Protocol Conversion Module

Product Specifications

| Technical specifications |  |
| --- | --- |
| Order No. | SRE6081 |
| Maximum number of slaves | 63 |
| Maximum inputs/outputs for a single slave | 128-byte |
| Baud rate support | 125kbit/s, 250kbit/s, 500kbit/s |
| Slave EDS | EDS files cannot be imported |
| Scanning slave support or not | Scan through configuration software |
| Matching resistance | An external 120 ohm resistor is required |
| DeviceNet side power supply | External 24VDC is required |
| Synchronization mode | Free to run |
| Network cycle time | As low as 100 μ s |
| Isolation |  |
| Between channel and bus | Yes |
| Display indication | Power supply green LED display |
| Diagnosis and alarm of system power supply | Support |
| Operating environment | Operating temperature: -20~60℃ , Relative humidity: 5%~90% (no condensation) |
| Dimension(L×W×H) | 24*100*80 |

Ordering data

| Specification | Order No. |
| --- | --- |
| The DeviceNet protocol conversion module supports a baud rate of up to 500 kbit/s | SRE6081 |

Profibus DP Protocol Conversion Module

Product Specifications

| Technical specifications |  |
| --- | --- |
| Order No. | SRE6091 |
| Maximum number of slaves | 125 slaves |
| Slave GSD file | Support importing GSD files |
| Prof i bus DP max. input and output bytes | 1400 bytes |
| Diagnostic Slave Functions | None |
| Prof i bus DP baud rate | 9.6Kbps , 19.2Kbps , 31.25Kbps , 45.45Kbps , 93.75Kbps , 187.5Kbps , 500Kbps, 1500Kbps , 3000Kbps , 6000Kbps , 12000Kbps |
| PROF I BUS DP interface | DB nine-pin interface |
| Matching resistor | 120 ohms (dip switch) |
| ES I file | Default |
| Maximum input and output length for EtherCAT | 512 bytes each |
| Network interface | EtherCAT IN and EtherCAT OUT |
| Synchronization mode | Free operation |
| Network cycle time | As low as 100 µs |
| Isolation |  |
| Between channel and bus | Yes |
| Display indication | Power supply green LED display |
| Diagnosis and alarm of system power supply | Support |
| Operating environment | Operating temperature: -20~60℃ , Relative humidity: 5%~90% (no condensation) |
| Dimension(L×W×H) | 24*100*80 |

Ordering data

| Specification | Order No. |
| --- | --- |
| Prof i bus DP protocol conversion module, support baud rate 9.6Kbps , 19.2Kbps , 31.25Kbps , 45.45Kbps, 93.75Kbps , 187.5Kbps , 500Kbps , 1500Kbps , 300Kbps0 , 6000Kbps , 12000Kbps | SRE6091 |

High-speed Counting Module

Product Features

● 2/4 groups of high-speed counters (A, B, C phases)

● Single-ended or differential inputs

● Relevant parameters can be configured through XML files

Product Specifications

| Technical specifications |  |  |
| --- | --- | --- |
| Order No. | SRE5012 | SRE5014 |
| High-speed counting channel | 2 channels (A, B, C, STOP/LATCH); Single-ended input max. 200KHZ, differential max. 4MHZ; Rated voltage 5VDC, 24VDC | 4 channels (A, B, C, STOP/LATCH); Differential up to 4 MHZ; Rated voltage 5 VDC |
| Bus 5VDC current consumption | ＜70mA |  |
| Cable length (shielded twisted pair) | Up to 100m |  |
| High-speed counter input characteristics | RS422 differential input |  |
| Signal input (data) | \ |  |
| Other input characteristics | Single-ended (rated 24V max 200KHZ), differential (5V max 4MHZ) | Differential (5V max 4MHZ) |
| Signal output (pulse) | \ |  |
| Data transmission speed | \ |  |
| Distributed cock | Support |  |
| Encoding method | \ |  |
| Encoder input rated voltage | 5V, 24V | 5V |
| High-speed counting mode | 1. Single-ended count, count the pulse of phase A, B is the direction, add the count if B is the high level, and reduce the count if B is the low level. 2. Differential counting, phase A and B pulses are orthogonal.. Add the count if A is ahead of phase B by 90°, and otherwise reduce the count. 3. If the master enables the function of setting the current count value, and the set counter is TRUE, the current count value is set to the preset value. 4. The master station enables the latch function, which can be set to the raising edge or falling edge latch, and the current count value is latched on the raising edge of the C phase and the raising edge or falling edge of the LATCH input terminal. |  |
| Isolation |  |  |
| Between channel and bus | Yes |  |
| Display indication | Power supply green LED display |  |
| Diagnosis and alarm of system power supply | Support |  |
| Operating environment | Operating temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |  |
| Dimension(L×W×H) | 24*100*80 |  |

Ordering data

| Specification | Order No. |
| --- | --- |
| High-speed count module, 2 sets of A, B, and C counting inputs, single-ended (rated 24V maximum 200KHZ, support PNP/NPN input) or differential (5V maximum 4MHZ), support ordinary count function, relevant parameters can be configured through XML files, SRE8200 can expand 64 modules. | SRE5012 |
| High-speed counting module, 4 sets of A, B, and C counting inputs, differential (5V maximum 4MHZ), support ordinary counting function, configure relevant parameters through XML documents, and SRE8200 can expand to 64 modules. | SRE5014 |

Pulse Output Module

Product Features

● 4-axis PTO output, configure relevant parameters through XML files

● NPN type output up to 400KHZ

● Differential output up to 1MHZ

Product Specifications

| Technical specifications |  |
| --- | --- |
| Order No. | SRE5234 |
| Module type | PTO output module |
| Number of PT0 output channels | 4-axis (pulse, direction) |
| PT0 output type | NPN |
| PT0 output frequency | Differential max. 1MHZ, single-ended max. 400KHZ (at 5V) |
| PT0 duty cycle adjustment range | 35%~60% random |
| Bus response time | Less than 500us |
| Cable length (shielded twisted pair) | Maximum 100m |
| Isolation |  |
| Between Channel to bus | Yes |
| Between power to bus | Yes |
| Diagnosis and alarm of system power supply | Support |
| Operating environment | Operating temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |
| Dimension(L×W×H) | 24*100*80 |

Ordering data

| Specification | Order No. |
| --- | --- |
| Pulse output module, 4-axis PT0 output, NPN type output up to 400KHZ (at 5V), differential output up to 1MHZ, relevant parameters can be configured through XML files, SRE8200 can expand to 64 modules. | SRE5234 |

Digital Fast Output Module

Product Features

● 2-way and 4-way output modules

● With DC clock and oversampling function

● The maximum output frequency is 1MHz

Product Specifications

| Technical specifications |  |  |
| --- | --- | --- |
| Order No. | SRE5202 | SRE5204 |
| Enclosure type | Plastic shell |  |
| Rated supply voltage | 24V DC |  |
| Load type | Resistive load, inductive load, lamp load |  |
| Oversampling factor | n = An integer multiple of the cycle time, 1...1000 |  |
| Distributed cock | << 1 µs |  |
| Maximum output current | 0.5 A per channel (short circuit protection) |  |
| Switching time | TON: < 1 µs, TOFF: < 1 µs |  |
| Maximum frequency | 1MHz |  |
| Cable length (shielded) | Maximum 500m |  |
| Cable length (unshielded) | Maximum 150m |  |
| Digital output characteristics |  |  |
| Output points | 2 | 4 |
| Output type | Transistor PNP output |  |
| Communication |  |  |
| Supported protocols | \ |  |
| Display indication | Power supply green LED display, channel disconnection alarm red LED display |  |
| Operating environment | Operating environment temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |  |
| Dimension(L×W×H) | 24*100*80 |  |

Ordering data

| Specification | Order No. |
| --- | --- |
| Digital fast output module with DC distributed clock and oversampling function, maximum output frequency of 1MHz, 2 outputs, transistor PNP type, rated 24VDC/0.5A, module diagnostic function, and SRE 8200 can expand to 64 modules. | SRE5202 |
| Digital fast output module with DC distributed clock and oversampling function, maximum output frequency of 1MHz, 4 outputs, transistor PNP type, rated 24VDC/0.5A, module diagnostics, and SRE 8200 can expand to 64 modules. | SRE5204 |

Power Relay Module

Product Specifications

| Technical specifications |  |
| --- | --- |
| Product name | Power relay module |
| Order No. | SRE9001 |
| Power Specifications |  |
| Input power voltage | 24V DC(±20%) |
| Output system voltage | 5V±5% (for module bus) |
|  | 24V±20% (expansion module power) |
| Output system current | ＜10A |
| Accreditation | -- |
| Physical properties |  |
| Dimension(L×W×H) | 12*100*80 |
| Operating environment | Operating environment temperature: -20~60℃, Relative humidity: 5%~90% (no condensation) |
| Storage temperature | -25~+85℃ |
| Relative humidity | 95%, no condensation |
| Protection class | IP20 |
| Occupied slot | Not occupied |
| Diagnosis and alarm of system power supply | Not Supported |

Ordering data

| Specification | Order No. |
| --- | --- |
| SRE9001 power relay module, 24VDC power relay, but also 5VDC isolated bus power relay, does not occupy slot, no system diagnosis, alarm function | SRE9001 |