Manual of SRE Series Products

Ver 1.2

Content

1. SRE800 coupler module	1

1.1. Electrical specifications	1

1.2. Wiring Diagram	2

1.3. Terminal Description	3

1.4. Description of Indicator	3

2. Digital Input Module	4

2.1. Electrical Specifications	4

2.2. Wiring Diagram	5

2.2.1. SRE1016 Wiring Diagram	5

2.2.2. SRE1032 Wiring Diagram	6

2.3. Interface Description	7

2.3.1. SRE1016 Wiring Terminal Description	7

2.3.2. SRE1032 Wiring Terminal Description	7

2.4. Indicator Description	7

2.4.1. SRE1016 Indicator Description	7

2.4.2. SRE1032 Indicator Description	7

2.5. COE General Parameter Description	8

3. Digital Output Module	9

3.1. 16 Point Digital Output Electrical Specifications	9

3.2. 32 Point Digital Output Electrical Specifications	11

3.3. Wiring Diagram	13

3.3.1. SRE2116 Wiring Diagram	13

3.3.2. SRE2216 Wiring Diagram	14

3.3.3. SRE2132 Wiring Diagram	15

3.3.4. SRE2232 Wiring Diagram	16

3.4. Indicator Description	17

3.4.1. SRE2216/SRE2116 Indicator Description	17

3.4.2. SRE2232/SRE2132 Indicator Description	17

3.5. COE General Parameter Description	18

4. Digital Input/Output Module	19

4.1. Electrical Specifications	19

4.2. Wiring Diagram	21

4.2.1. SRE1332 Wiring Diagram	21

4.2.2. SRE1432 Wiring Diagram	22

4.3. Indicator Description	23

4.4. COE General Parameter Description	23

5. Analog Rapid Acquisition Input Module	25

5.1. Electrical Specifications	25

5.2. SRE3522 Module Wiring Diagram	26

5.3. Indicator Description	27

5.4. Terminal Description	27

5.5. Parameter Description	28

6. Analog Input Module	29

6.1. Electrical Specifications	29

6.2. Module Wiring Diagram	30

6.2.1. SRE3204 Wiring Diagram	30

6.2.2. SRE3208 Wiring Diagram	31

6.3. Terminal Description	32

6.4. Indicator Description	32

6.5. COE General Parameter Description	33

7. Analog Output Module	34

7.1. Electrical Specifications	34

7.2. Module Wiring Diagram	35

7.2.1. SRE4204 Wiring Diagram	35

7.2.2. SRE4208 Wiring Diagram	36

7.3. Indication Description	37

7.4. Terminal Description	37

7.4.1. SRE4204 Terminal Description	37

7.4.2. SRE4208 Terminal Description	37

7.5. COE General Parameter Description	38

8. Usage Example	39

8.1. SRE8200 Coupler and Communication Instructions with BECKHOFF Main Station	39

8.1.1. Communication Connection	39

8.1.2. Hardware Configuration	39

8.1.3. Install XML files	40

8.1.4. New Project and Configuration	40

8.1.5. Data Monitoring	42

8.2. Communication Example between SRE2116 and TwinCAT3	43

8.2.1. Communication Connection	43

8.2.2. Hardware Configuration	43

8.2.3. Install XML files	44

8.2.4. New Project and Configuration	44

8.2.5. Data Monitoring	45

8.3. Communication Example between SRE3204 and TwinCAT3	46

8.3.1. Communication Connection	46

8.3.2. Hardware Configuration	46

8.3.3. Install XML files	47

8.3.4. New Project and Configuration	47

8.3.5. Data Monitoring	49

8.4. Communication Example between SRE3522 and TwinCAT3	50

8.4.1. Communication Connection	50

8.4.2. Hardware Configuration	50

8.4.3. Install XML file	51

8.4.4. New Project and Configuration	51

8.4.5. Data Monitoring	53

Appendix Configuration Parameter Description	54

TwinCAT3 startup Feature Description	54

Codesys Startup Parameter Setting Extension Module Parameter Description	57

Description of Sysmac Studio Initialization Parameter Setting Function	58

| Manual version | Description |
| --- | --- |
| V1.0 | Initial version. |
| V1.1 | Update product, add product description of SRE1032, SRE2322, SRE2132, SRE1332, SRE1432, SRE3208, and SRE4208 |
| V1.2 | Add product description of SRE3522 |

SRE800 coupler module

Electrical specifications

| Model | SRE8200 coupler module |
| --- | --- |
| Product overview | 2 RJ45 interfaces, stable 24VDC power supply performance, strong anti-interference performance |
| Technical specifications |  |
| Order No. | SRE8200 |
| Electrical interface | RJ45 |
| Working power supply | 20.8~28.8V DC |
| Is the CPU connected? | No (independent slave) |
| Support agreement | EtherCAT Slave |
| Quantity of built-in IO | NA |
| Station Settings |  |
| Address setting | Configure by dip switch or main station |
| Maximum quantity of stations per segment | 255 |
| Isolation |  |
| Between channel and bus | Yes |
| Power supply to bus | Yes |
| Display indication | Power supply+24V green light, SF red light, NET red light |
| System power diagnosis and warning | Support |
| Operating environment | Working environment temperature: -10 ～ 55 °C; Relative humidity: 5% to 90% (no condensation) |
| Dimensions (length x width x height) | 48×80×100mm |

Wiring Diagram

Figure 1-2

Note: Us is the power terminal of the coupler, and Up is the power terminal of the expansion module.

Terminal Description

| Wiring terminals | Description |
| --- | --- |
| Up_24V | Positive electrode of coupler power supply terminal |
| Up_0V | Negative electrode of coupler power supply terminal |
| Us_24V | Positive electrode of expansion module power supply terminal |
| Us_0V | Negative electrode of expansion module power supply terminal |

Description of Indicator

| Indicator | Description |
| --- | --- |
| PWR (green) | Coupler power indicator: On: module power supply is normal; Off: The module is not powered or its power supply is abnormal. |
| PWR_IO (green) | IO power indicator: On: IO power supply is normal Off: IO is not powered or its power supply is abnormal |
| BF (red) | Bus fault indicator: Always on: Configuration error Off: The module functions properly |
| RUN (yellow) | Bus communication indicator: Flashing: Module is normal Off: Communication malfunction |

Digital Input Module

High performance digital input module, 16/32 digital input, NPN/PNP input, 24VDC, with module diagnostic function

Electrical Specifications

| Model | SRE1016 | SRE1032 |
| --- | --- | --- |
| Technical specifications |  |  |
| Input points | 16 | 32 |
| Cable length (unshielded) | 100m |  |
| Input characteristics | Source type, leakage type |  |
| Allowable static current | 1mA |  |
| Insulation test voltage | 500V DC |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| - Between channels | Yes |  |
| Display indication | Green LED display for each channel input |  |
| System power diagnosis and warning | Support |  |
| Working temperature | Working environment temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 15×80×100 mm | 30×80×100 mm |

Wiring Diagram

SRE1016 Wiring Diagram

NPN wiring

NPN wiring

PNP wiring

PNP wiring

SRE1032 Wiring Diagram

NPN wiring

NPN wiring

PNP wiring

PNP wiring

Interface Description

SRE1016 Wiring Terminal Description

| Terminal | Description |
| --- | --- |
| Input1~Input16 | Module input terminal |
| COM1, COM2 | Input public end |

SRE1032 Wiring Terminal Description

| Terminal | Description |
| --- | --- |
| Input1~Input32 | Module input terminal |
| COM1, COM2 | Input public end |

Indicator Description

SRE1016 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR | Module power indicator: On: Module power supply is normal Off: No power supply or abnormal power supply |
| NET | Communication indicator: On: Communication is normal Off: Communication is abnormality |
| I1~I16 (green) | Digital input indicator, the corresponding indicator lights up when the input channel detects a signal. |

SRE1032 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR | Module power indicator: On: Module power supply is normal Off: Module has no power supply or abnormal power supply |
| NET | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| I1~I32 (green) | Digital input indicator, the corresponding indicator lights up when the input channel detects a signal. |

COE General Parameter Description

Module related parameters can be viewed or modified in COE parameters, and parameter are set not saved when powered off.

| Parameter | Description |
| --- | --- |
| 2002:01 LocalDI | Parameters are used to set the digital input module and DI delay None: No delay 1.6ms: DI delay is 1.6ms 3.2ms: DI delay is 3.2ms 12.8ms: DI delay is 12.8ms 20ms: DI delay is 20ms 50ms: DI delay is 50ms |
| 2003:01 Fliter time | None: No filtering; 1:1ms； 2:2ms； 3:5ms； 4:10ms； 5:20ms； 6: 50ms. |
| 2004:01 Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |

Digital Output Module

16 Point Digital Output Electrical Specifications

SRE2216/SRE2116 digital output module, 16 channel digital output, with built-in DO and module diagnostic function.

| Model | SRE2216 | SRE2116 |
| --- | --- | --- |
| Technical specifications |  |  |
| Type of output | PNP solid-state MOSFET | NPN solid-state MOSFET |
| Output points | 16 |  |
| Bus consumption current (at 24VDC full load) | 29.4mA | 84.6mA |
| Cable length (unshielded) | 100m |  |
| Output short-circuit protection | Yes, electronic |  |
| Maximum lamp load | 5W |  |
| Output current “1” | 0.5A |  |
| Leakage current | ＜1mA |  |
| Switching frequency |  |  |
| - Resistive load, maximum | 100HZ |  |
| - Inductive load, maximum | 0.5HZ |  |
| - Lamp load, maximum | 10HZ |  |
| - Mechanical load, maximum | --- |  |
| Insulation test voltage | 500V DC |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| - Between channels | Yes |  |
| Display indication | Each channel outputs a green LED display |  |
| System power diagnosis and warning | Support |  |
| Working temperature | Working environment temperature: -20~60 ℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 15×80×100 mm |  |

32-Point Digital Output Electrical Specifications

| Model | SRE2232 | SRE2132 |
| --- | --- | --- |
| Technical specifications |  |  |
| Type of output | PNP solid-state MOSFET | NPN solid-state MOSFET |
| Output points | 32 |  |
| Bus consumption current (at 24VDC full load) | 29.4mA | / |
| Cable length (unshielded) | 100m |  |
| Output short-circuit protection | Yes, electronic |  |
| Maximum lamp load | 5W |  |
| Output current “1” | 0.5A |  |
| Leakage current | ＜1mA |  |
| Switching frequency |  |  |
| - Resistive load, maximum | 100HZ |  |
| - Inductive load, maximum | 0.5HZ |  |
| - Lamp load, maximum | 10HZ |  |
| - Mechanical load, maximum | --- |  |
| Insulation test voltage | 500V DC |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| - Between channels | Yes |  |
| Display indication | Each channel outputs a green LED display |  |
| System power diagnosis and warning | Support |  |
| Working temperature | Working environment temperature: -20~60 ℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 30×80×100 mm |  |

Wiring Diagram

SRE2116 Wiring Diagram

SRE2216 Wiring Diagram

SRE2132 Wiring Diagram

SRE2232 Wiring Diagram

Indicator Description

SRE2216/SRE2116 Indicator Description

| Indicator | Description |
| --- | --- |
| PWR | On: The module power supply is normal; Off: The module is powered off; |
| NET | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| LED1~LED16 | Digital output indicator, the corresponding indicator lights up when a signal is detected. |

SRE2232/SRE2132 Indicator Description

| indicator | Description |
| --- | --- |
| PWR | On: The module power supply is normal; Off: The module is powered off; |
| NET | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| LED1~LED32 | Digital output indicator, the corresponding indicator lights up when a signal is detected. |

COE General Parameter Description

| Parameter | Description |
| --- | --- |
| 2001:01 EtherCATBusErrOutoutEN | The parameter is used to set the action of output channel after the module communication is disconnected (this setting will not be saved in case the power is turned off): 0: Maintain the output for 50ms and then clear it; 1: Maintain output; 2: Clear after maintaining the output for 10ms; 3: Clear after maintaining the output for 20ms; 4: Clear after maintaining output for 100ms; 5: Clear after maintaining the output for 500ms; 6: Clear the output immediately; |
| 2004:01 Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. Bit1: Reserved; Bit2: 1: DO short circuit or overcurrent; 0: Normal. |

Digital Input/Output Module

Electrical Specifications

SRE digital input/output module, 16 digital inputs, 16 digital outputs, NPN/PNP type, module with diagnostic function.

| Model | SRE1332 |  | SRE1432 |
| --- | --- | --- | --- |
| Technical specifications |  |  |  |
| Bus 24V current consumption (at full load) | 89.7mA | 33.5mA |  |
| Input characteristics |  |  |  |
| Input points | 16 |  |  |
| - Limit value | 24V DC |  |  |
| - Signal “0” | Maximum 5V DC, 1mA |  |  |
| - Signal “1” | Minimum 15V DC, 2.5mA |  |  |
| Input characteristics | Leakage type | Source type |  |
| Allowable static current | 1mA |  |  |
| Insulation test voltage | 500V DC |  |  |
| Cable length (unshielded) | Maximum length of 300m |  |  |
| Cable length (shielding) | Maximum length of 500m |  |  |
| Output |  |  |  |
| Type of output | NPN solid-state MOSFET | PNP solid-state MOSFET |  |
| Output points | 16 |  |  |
| Cable length (unshielded) | Maximum length of 300m |  |  |
| Cable length (shielding) | Maximum length of 500m |  |  |
| Output short-circuit protection | Yes, electronic |  |  |
| Maximum lamp load | 5W |  |  |
| Output current “1” | 0.5A |  |  |
| Leakage current | ＜1mA |  |  |
| Contact mechanical lifespan | -- |  |  |
| Contact electrical life (rated load) | -- |  |  |
| Switching frequency |  |  |  |
| - Resistive load, maximum | 100HZ |  |  |
| - Inductive load, maximum | 0.5HZ |  |  |
| - Lamp load, maximum | 10HZ |  |  |
| - Mechanical load, maximum | -- |  |  |
| Insulation test voltage | 500V DC |  |  |
| Isolation |  |  |  |
| - Between channel and bus | Yes |  |  |
| - Between channels | Yes |  |  |
| Display indication | Each channel outputs a green LED display |  |  |
| System power diagnosis and warning | Support |  |  |
| Working temperature | Working environment temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |  |
| Dimensions (length x width x height) | 30×80×100 mm |  |  |

Wiring Diagram

SRE1332 Wiring Diagram

SRE1432 Wiring Diagram

Indicator Description

| Indicator | Description |
| --- | --- |
| PWR | On: The module power supply is normal; Off: The module is powered off; |
| NET | Communication indicator: On: Communication is normal Off: Communication is abnormal |
| I1~I16 | The digital input indicator will turn on when a signal is detected. |
| Q1~Q16 | Digital output indicator, the corresponding indicator lights up when a signal is detected. |

COE General Parameter Description

| Parameter | Description |
| --- | --- |
| 2001:01 EtherCATBusErrOutoutEN | Parameters are used to set the action of the output channel after the module communication is disconnected: 0: Maintain the output for 50ms and then clear it; 1: Maintain output; 2: Clear after maintaining the output for 10ms; 3: Clear after maintaining the output for 20ms; 4: Clear after maintaining the output for 100ms; 5: Clear after maintaining the output for 500ms; 6: Clear the output immediately; |
| 2002:01 LocalDI | Parameters are used to set the digital input module and DI delay None: No delay 1.6ms: DI delay is 1.6ms 3.2ms: DI delay is 3.2ms 12.8ms: DI delay is 12.8ms 20ms: DI delay is 20ms 50ms: DI delay is 50ms |
| 2003:01 Fliter time | None: No filtering; 1:1ms； 2:2ms； 3:5ms； 4:10ms； 5:20ms； 6: 50ms. |
| 2004:01 Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. Bit1: Reserved; Bit2: 1: DO short circuit or overcurrent; 0: Normal. |

Analog Rapid Acquisition Input Module

SRE3522 two-way analog fast acquisition module, does not support Omron platform.

Electrical Specifications

| Model | SRE3522 |
| --- | --- |
| Technical specifications |  |
| Supply voltage | 18~28V DC |
| Number of input channels | 2 |
| Collection type | Voltage |
| Range |  |
| Voltage | -10V-10V |
| Data word |  |
| Bipolar | -32000~32000 |
| Resolution | 16 bits |
| Input type | Differential input |
| Sampling type | Simultaneously |
| Oversampling coefficient | N=1... 100 optional (up to 100 ksamples/s) |
| Maximum sampling rate | Maximum 10 µ s/100 ksps (per channel, synchronous) |
| Isolation |  |
| - Between channel and bus | Yes |
| Display indication | Power supply green LED display |
| Distributed clock | Support |
| System power diagnosis and warning | Support |
| Operating environment |  |
| Working temperature | Working environment temperature: -20~60 ℃, relative humidity: 5%~90% (no condensation) |
| Anti-vibration/anti-impact performance | Comply with EN 60068-2-6/EN 60068-2-27 standards |
| Anti-electromagnetic interference/anti- electromagnetic radiation performance | Comply with EN 61000-6-2/EN 61000-6-4 standards |
| Dimensions (length x width x height) | 15×80×100 mm |

SRE3522 Module Wiring Diagram

①Three wire sensor    ③ Four wire sensor

*Short circuit between negative signal and negative power supply during single wire connection

Voltage transmitter

Voltage transmitter

Indicator Description

| Indicator | Description |
| --- | --- |
| PWR (green) | Module power indicator: On: Power supply is normal Off: Abnormal power supply or module not powered |
| NET (green) | Communication indicator: On: Communication is normal Off: Communication is abnormal |

Terminal Description

| Terminal | Description |
| --- | --- |
| A+,A- | CH0 voltage acquisition input terminal |
| B+,B- | CH1 voltage acquisition input terminal |

Parameter Description

The signal oversampling period is: Sample Cycle Time=Sync Unit Cycle Time/Oversampling Factor, with a minimum sampling period of 10us, for sampling. Example: If the bus cycle time is 1000us and the sampling frequency is 100 times, then the sampling period is 10us. A value is sampled per 10 us and execute 100 times, and this data is accumulated and transmitted in the next bus cycle.

| Parameter | Description |
| --- | --- |
| Operation Mode: | Select the number of channels used: 2 Channels: Select two channels 1 Channel: Select one channel (first channel) |
| Sync Unit Cycle Time (us): | Cycle time, determined by EtherCAT's set cycle time |
| Oversampling Factor: | Sampling frequency per cycle: up to 100 times can be collected 1:1 2:2 3:4 4:5 5:8 6:10 7:16 8:20 9:25 10:32 11:40 12:50 13:64 14:80 15:100 |
| Sample Cycle Time (us): | The sampling cycle is determined by the relationship between the EtherCAT set cycle and the quantity of samples |

Analog Input Module

Electrical Specifications

High performance analog input module, 16 bit accuracy, 4/8 channel voltage/current input, with module diagnostic function.

| Model | SRE3204 | SRE3208 |
| --- | --- | --- |
| Technical specifications |  |  |
| Supply voltage | 18~28V DC |  |
| Number of input channels | 4 | 8 |
| Input type | Voltage/Current |  |
| Range |  |  |
| Voltage (unipolar) | 0-10V |  |
| Voltage (Bipolar) | -10V-10V |  |
| Current | 0~20mA |  |
| Data word |  |  |
| Unipolar | 0~32000 |  |
| Bipolar | -32000~32000 |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| Display indication | Power supply green LED display |  |
| System power diagnosis and warning | Support |  |
| Working temperature | Working environment temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 15×80×100 mm | 30×80×100 mm |

Module Wiring Diagram

SRE3204 Wiring Diagram

Channel 3

Channel 2

Channel 1

Channel 0

Voltage transmitter

Voltage transmitter

Current transmitter

Current transmitter

①Three wire sensor ②Two wire sensor   ③ Four wire sensor

*Short circuit between negative signal and negative power supply during single wire connection

Note: A+ and A - are voltage signal input channels, and AI+and AI current signal input channels. If CH0 needs to be connected to a voltage signal, it shall be connected with A+ and A - terminals; If CH0 needs to be connected to a current signal, it shall be connected with the AI+and AI - terminals; These two channels are both CH0 and occupy the same data address, so only one can be used and cannot be connected simultaneously. The other input channels follow this rule. The wiring on the diagram is only an example, and the specific usage can be connected according to one’s own needs.

SRE3208 Wiring Diagram

Current transmitter

Current transmitter

Voltage transmitter

Voltage transmitter

①Three wire sensor ②Two wire sensor   ③ Four wire sensor

*Short circuit between negative signal and negative power supply during single wire connection

Note: A+ and A - are voltage signal input channels, and AI+and AI current signal input channels. If CH0 needs to be connected to a voltage signal, it shall be connected with A+ and A - terminals; If CH0 needs to be connected to a current signal, it shall be connected with the AI+and AI - terminals; These two channels are both CH0 and occupy the same data address, so only one can be used and cannot be connected simultaneously. The other input channels follow this rule. The wiring on the diagram is only an example, and the specific usage can be connected according to one’s own needs.

Terminal Description

| Terminal | Description |
| --- | --- |
| A+,A- | CH0 voltage input terminal |
| AI+,AI- | CH0 current input terminal |
| B+,B- | CH1 voltage input terminal |
| BI+,BI- | CH1 current input terminal |
| C+,C- | CH2 voltage input terminal |
| CI+,CI- | CH2 current input terminal |
| D+,D- | CH3 voltage input terminal |
| DI+,DI- | CH3 current input terminal |

Indicator Description

| Indicator | Description |
| --- | --- |
| PWR | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| NET | Communication indicator: On: Communication is normal Off: Communication is abnormal |

COE General Parameter Description

The configuration parameters will not be synchronized to Startup, and they will not be saved after power failure or hot plugging.

| Parameter | Data type | Description |
| --- | --- | --- |
| 2004:01 | Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |
| 2005:01 | Channel Num | 0: Enable 4 channels; 1: Enable the first channel; 2: Enable the first two channels; |
| 2005:02 | Channel Time | Channel update time: 0:400us； 1:lms； 2:2ms； 3:5ms； 4:10ms； 5:20ms； |
| 2005:03 | Channel Type | Each BIT corresponds to a channel: for example, Bit0: corresponds to CH0; Bit1: corresponds to CH1; ........ Set detection value: 0: Voltage ± 10V; 1: Current 0-20mA; |

Analog Output Module

Electrical Specifications

SRE4204 analog output module, 4-channel voltage/ current, ± 10V or 0-20mA, module diagnostic function, 16 bit accuracy, 35mm rail installation.

| Model | SRE4204 | SRE4208 |
| --- | --- | --- |
| Supply voltage | 18~28V DC |  |
| Number of output channels | 4 | 8 |
| Range |  |  |
| Voltage (unipolar) | 0~10V |  |
| Voltage (Bipolar) | -10~10V |  |
| Current | 0~20mA |  |
| Voltage | -32000~32000, full range |  |
| Current | 0~32000, full range |  |
| Isolation |  |  |
| - Between channel and bus | Yes |  |
| Display indication | Power supply green LED display |  |
| System power diagnosis and warning | Support |  |
| Working temperature | Working environment temperature: -20~60℃, relative humidity: 5%~90% (no condensation) |  |
| Dimensions (length x width x height) | 15×80×100 mm | 30×80×100 mm |

Module Wiring Diagram

SRE4204 Wiring Diagram

Voltage load of channel 2

Current load of channel 1

Voltage load of channel 1

Current load of channel 3

Current load of channel 2

Voltage load of channel 3

Current load of channel 0

Voltage load of channel 0

SRE4208 Wiring Diagram

Current load of channel 7

Current load of channel 6

Current load of channel 5

Current load of channel 4

Voltage load of channel 4

Voltage load of channel 3

Current load of channel 3

Current load of channel 2

Current load of channel 1

Current load of channel 0

Voltage load of channel 5

Voltage load of channel 6

Voltage load of channel 7

Voltage load of channel 2

Voltage load of channel 1

Voltage load of channel 0

Indication Description

| Indicator | Description |
| --- | --- |
| PWR | Module power indicator: On: The module power supply is normal; Off: The module is powered off; |
| NET | Communication indicator: On: Communication is normal Off: Communication is abnormal |

Terminal Description

SRE4204 Terminal Description

| Terminal | Description |
| --- | --- |
| V0,M0 | CH0 voltage output terminal |
| I0,M0 | CH0 current output terminal |
| V1,M1 | CH1 voltage output terminal |
| I1,M1 | CH1 current output terminal |
| V2,M2 | CH2 voltage output terminal |
| I2,M2 | CH2 current output terminal |
| V3,M3 | CH3 voltage output terminal |
| I3,M3 | CH3 current output terminal |

SRE4208 Terminal Description

| Terminal | Description |
| --- | --- |
| V0,M0 | CH0 voltage output terminal |
| I0,M0 | CH0 current output terminal |
| V1,M1 | CH1 voltage output terminal |
| I1,M1 | CH1 current output terminal |
| V2,M2 | CH2 voltage output terminal |
| I2,M2 | CH2 current output terminal |
| V3,M3 | CH3 voltage output terminal |
| I3,M3 | CH3 current output terminal |
| V4,M4 | CH4 voltage output terminal |
| I4,M4 | CH4 current output terminal |
| V5,M5 | CH5 voltage output terminal |
| I5,M5 | CH5 current output terminal |
| V6,M6 | CH6 voltage output terminal |
| I6,M6 | CH6 current output terminal |
| V7,M7 | CH7 voltage output terminal |
| I7,M7 | CH7 current output terminal |

COE General Parameter Description

| Parameter | Data type | Description |
| --- | --- | --- |
| 2001:01 | EtherCATBusErrOutputEN | Parameters are used to set the action of the output channel after the module communication is disconnected: 0: Maintain the output for 50ms and then clear it; 1: Maintain output; 2: Clear after maintaining the output for 10ms; 3: Clear after maintaining the output for 20ms; 4: Clear after maintaining output for 100ms; 5: Clear after maintaining the output for 500ms; 6: Clear the output immediately; |
| 2004:01 | Err 24v_nf | Bit0: 1: Channel 24V power supply is abnormal; 0: Normal. |
| 2005:01 | Channel Type | Each BIT corresponds to a channel: for example, Bit0: corresponds to CH0; Bit1: corresponds to CH1; ........ Set channel range configuration: 0:±10V 1:0-20mA/0-10V |

Usage Example

SRE8200 Coupler and Communication Instructions with BECKHOFF Main Station

Communication Connection

Communication connection diagram is as shown followings:

Note:

- Each module has its own corresponding XML file, which needs to be added before it can be used.

Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE1116 | 1 piece | Digital input module |
| SRE2116 | 1 piece | Digital output module |
| SRE3204 | 1 piece | Analog input module |
| SRE4204 | 1 piece | Analog output module |
| Network cable | Some |  |
| 24V Switching Power Supply | 1 piece |  |

Install XML files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT” as shown in the following figure:

New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan the SRE8200 and its extended IO connected to the computer into the project, click I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

Data Monitoring

Select the IO terminal to be monitored on TwinCAT3 and choose the data to be monitored:

Digital input/output:

Analog input/output:

Communication Example between SRE2116 and TwinCAT3

Communication Connection

Communication connection diagram is shown as follows:

Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE2116 | 1 piece | High performance digital output module |
| SRE1116 | 1 piece | High performance digital input module |
| Network cable | 1 item |  |
| 24V Switching Power Supply | 1 piece |  |

Install XML files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

Note: High performance modules have their own corresponding XML files, which need to be added before they can be used.

New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan the ECT coupler SRE8200 and its extension IO connected to the computer into the project, click I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

Data Monitoring

Select the IO terminal to be monitored on TwinCAT3 and choose the data to be monitored:

Communication Example between SRE3204 and TwinCAT3

Communication Connection

Communication connection diagram is shown as follows:

Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE3204 | 1 piece | High performance analog input module |
| SRE4204 | 1 piece | High performance analog output module |
| Network cable | 1 item |  |
| 24V switching power supply | 1 piece |  |

Install XML files

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

Note: High performance modules have their own corresponding XML files, which need to be added before they can be used.

New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan the SRE8200 and its extension IO connected to the computer into the project, click on I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

Data Monitoring

Select the IO terminal to be monitored on TwinCAT3 and choose the data to be monitored:

Communication Example between SRE3522 and TwinCAT3

Communication Connection

Communication connection diagram is shown as follows:

Hardware Configuration

The hardware configuration is shown in the following table:

| Hardware | Quantity | Notes |
| --- | --- | --- |
| Programming computer | 1 unit | Install TwinCAT3 software |
| SRE8200 | 1 piece | EtherCAT communication coupler |
| SRE3522 | 1 piece | Analog rapid acquisition module |
| Signal generator | 1 piece |  |
| Network cable | 1 item |  |
| 24V Switching Power Supply | 1 piece |  |

Install XML file

Install XML files into TwinCAT3, the default folder in the example is

“C:\TwinCAT\3.1\Config\Io\EtherCAT”, as shown in the following figure:

Note: High performance modules have their own corresponding XML files, which need to be added before they can be used.

New Project and Configuration

Open TwinCAT3 software and create a new project as shown in the following figure:

Scan the SRE8200 and its extension IO connected to the computer into the project, click on I/O>Devices>Scan, as shown in the following figure:

The successfully scanned module is shown in the following figure:

Data Monitoring

Select the desired channel on TwinCAT3 for data monitoring:

- Appendix Configuration Parameter Description

  - TwinCAT3 startup Feature Description

The parameters of the expansion module are not saved in COE. Every time the expansion IO terminal is rescanned or powered on again, the configuration of the expansion IO terminal will be restored to its factory settings. Set the parameters of the extension IO terminal in the startup item, and write the parameters to the coupler every time communication occurs. In the same project, when powered on repeatedly, the parameter configuration of the extension module remains unchanged.

For example, configure the CH1-CH4 channel range of SRE4204 to 0-20mA/0-10V.

After the parameter configuration is completed, it is necessary to refresh and update the data to COE parameters. Then the parameters will take effect and remain in effect after power failure. After rescanning the device, the settings will be restored to the original configuration.

Note: When configuring parameters for SRE3204/SRE3208, different parameters can only be configured in different parameter directories. For example, clicking the first parameter directory will set the first parameter in the parameter directory, and clicking the second parameter directory will set the second parameter in the parameter directory. If the same parameter is configured under three directory parameters, it will be replaced by the last parameter and the last configured parameter will be executed.

  - Codesys Startup Parameter Setting Extension Module Parameter Description

The parameters of the expansion module do not have a saving function. Every time the expansion IO terminal is rescanned or powered on again, the configuration of the expansion IO terminal will be restored to its factory settings.

Set the parameters of the extension IO terminal in the startup item, and write the parameters to the coupler every time communication occurs. In the same project, when powered on repeatedly, the parameter configuration of the extension module remains unchanged.

Scan device, click the module where the parameters need to be modified, select the startup parameters, and view the content of the parameters that can be changed.

Click the dropdown menu to modify parameters, and the downloaded parameters will take effect after the modification is completed.

  - Description of Sysmac Studio Initialization Parameter Setting Function

The parameters of the expansion module do not have a saving function. Every time the expansion IO terminal is rescanned or powered on again, the configuration of the expansion IO terminal will be restored to its factory settings. Set the parameters of the extension IO terminal in the startup item, and write the parameters to the coupler every time communication occurs. In the same project, when powered on repeatedly, the parameter configuration of the extension module remains unchanged.

After scanning the device, click the module where the parameters need to be modified, and select Edit Initialization Parameter Settings.

Select parameters through the dropdown menu.