Manual of SF1000 Local IO

Copyright Statement

This manual is owned by SINSEGYE. Without written permission, no one is allowed to copy, distribute, translate or otherwise use all or part of the content of this manual in any form.

This manual is protected by copyright law. Any reproduction, distribution, translation, display, performance, interpretation or use of the content of this manual, for any purpose, shall be definitely permitted by SINSEGYE. Without permission, any action shall be deemed as infringement of the copyright of SINSEGYE.

SINSEGYE reserves the right to update this manual at any time and without any notice. SINSEGYE shall not be liable for any loss or damage caused by the use or reliance on information contained or not explicitly stated in this manual.

When using this manual, you must comply with laws and regulations of all applicable countries (regions). It is forbidden to use this manual for illegal activities or violate any ethical guidelines.

Contents

I. Background	4

II. Experimental devices and models	4

III. Experimental wiring diagram	5

IV. Experimental steps	5

(I) Create a new project	5

(II) Connect the devices	5

(III) Add the device description file	5

(IV) Add local IO plugins	6

(V) Add local IO modules	12

(V) Digital I/O module test	13

(VII) Switching display of code value and data of analog quantity	16

(VIII) Pulse module test	21

1. Pulse module indicator test	21

2. Connection test of the pulse module and the encoder	25

Manual of SF1000 Local IO

I. Background

The plugin I/O modules adopt the combined structure of coupler module, power module and I/O module. The coupler is used to connect the extensible I/O modules to the real-time industrial Ethernet system, the backplane adopts SC-bus, and the coupler module is responsible for the field bus communication, thus realizing the function of real-time data exchange between various I/O modules and the couplers/controllers.

In this experiment, the metafacture1.0.4.0 is used to connect SX5 iComputer and plugin IO modules, to verify the real-time data exchange function between IO modules and controller.

II. Experimental devices and models

1. Hardware:

• SX5 series iComputer

• IO modules and others

| Module type | Product |
| --- | --- |
| N32 device provided by the manufacturer | N32 |
| Digital I/O module | RC2116 16-channel digital output module, NPN type, 24VDC, 0.5A |
|  | SRC2216 16-channel digital output module, PNP type, 24VDC, 0.5A |
|  | SRC1116 16-channel digital input module, NPN type, 24VDC, 3ms filtering |
|  | SRC1216 16-channel digital input module, PNP type, 24VDC, 3ms filtering |
|  | SRC3118 8-channel analog voltage input module |
|  | SRC3138 8-channel analog current input module |
|  | SRC4018 8-channel analog voltage output module |
|  | SRC4038 8-channel analog current output module |
| Temperature acquisition module | SRC3804 4-channel thermal resistance and thermocouple temperature acquisition module |
| Function module | SRC5001 24V single-ended incremental encoder counting module |
|  | SRC5031 5V differential incremental encoder counting module |
|  | SRC5041 SSI encoder counting module |
|  | SRC6041 RS485/RS422/RS232 gateway module |

2. Software: metafacture1.0.4.0

III. Experimental wiring diagram

Power port

Network port

As shown above, connect the network cable to the network port and the power supply to the power port. When N32 module is connected to the power supply, the iComputer will also be powered on.

IV. Experimental steps

(I) Create a new project

Create a new standard project. Please refer to this document for details.

(II) Connect the devices

1. Connect the display screen to the iComputer and check its IP address. Please refer to the IP address of the iComputer for details.

2. Connect the PLC by entering the IP address in the metafacture. For details, please refer to Connecting the PLC.

(III) Add the device description file

Add the following device description files for local IO. For details, please refer to this document for add/delete/export devices localIoDrv.devdesc.xml.

(IV) Add local IO plugins

1. Method I: Local update (Note: the metafacture software shall be shut down in this method).

1) In the “Start” menu, find "metafacture plugin manager" in the metafacture folder and open it, as shown below.

2) Download and decompress the local IO plugin installation package.

[sinsegye.ide.localioconfiguration.plugin (1).zip]

3) Open "Meta-fact Plugin Manager" and click "install plug", as shown below.

4) In the pop-up interface, select the extracted file "sinsegye.ide.localioconfiguration.plugin.dll", and click “Open”, as shown below.

5) At this time, the local IO plugin 1.0.0.2 will appear in the interface, and click “Close”, as shown below.

6) Click [profiles], find "sinsegye.ide.localioconfiguration", double-click to open it, and click [newst version] - [OK] in the pop-up window, as shown below.

The final result is as follows; click [close].

2. Method II: Online update

1) Click “Tools” – “Online Update Tool” in the menu bar.

2) Click "test" in the pop-up window, find "sinsegye.ide.localioconfiguration.plugin" and install it, as shown below.

3) Open the metafacture again and select “application”- “Add Object” – “Local IO Configuration Interface”, as shown below.

4) Click “Add” in the pop-up interface, and click OK, as shown below.

5) The following interface will pop up in the metafacture, indicating that it is added successfully.

(V) Add local IO modules

1. As shown below, the related IO modules have been connected behind the iComputer.

X5 iComputer(integrate N32)

2. Open the "Local IO Configuration Interface" in the metafacture, and drag the corresponding modules in turn in the IO module area on the right (Note: the dragging order must be the same as that of the actual hardware devices), as shown below.

3. Click "Generate Code" - "Login" - "Start", and you can also see that the added modules turn green (if it doesn't turn green, please check the module order), as shown below.

(V) Digital I/O module test

1. When the hardware of the devices is connected and the "Local IO Configuration Interface" is running, you can view the parameters of 2116 and 1116 respectively, as shown below.

"SRC2116" is a digital output module, which means that the module can receive and send the data from the iComputer.

"SRC1116" is a digital input module, which means that this module can receive data from other output modules, and its corresponding indicator will be turned on.

2. Hardware connection diagram

As shown above, connect the 2# channel of the 2116 module with the 11# channel of the 1116 module.

3. Open the metafacture, enter iogvl.MI_1116_1 in the code area of "PLC_PRG", in order to reference the variables of the IO module. Run the program, open the "IOGVL" interface, assign the value of the 5# channel of 2116 to True and write it; the 11# channel of random 1116 will become True, as shown below.

The renderings of hardware devices are as follows, the corresponding indicators have been turned on.

(VII) Switching display of code value and data of analog quantity

1. Add the relevant analog hardware module to the iComputer, as shown below. In this case, SRC3138 8-point analog input and SRC4038 8-channel current output are selected.

2. Add the corresponding IO modules in the metafacture, as shown below (Note: ensure the consistency with the physical order).

3. Click [Generate Code] – [Login] – [Run]; you can see that the modules have turned green in “Local IO Configuration Interface”, as shown below.

4. Code value display

- Click [Local IO Configuration Interface] – [Channel Basic Parameters], and you can see that 0~20mA (0~65535) is displayed in the range column, in which the values in brackets are called code values.

- The code value is a special numerical value in the industrial field, and the code value display means that the input and output display numbers are 0~65535 in the running state.

Code value correspondence table

|  | SRC4038 8-channel current output | SRC3138 8-point analog input |
| --- | --- | --- |
| Range | 0~20mA (0~65535) 4~20mA (0~65535) | 0~20mA (0~65535) 4~20mA (0~65535) |
| Corresponding value | 0 | 0 |
| Corresponding value | 65535 | 65535 |
| Range | 0~20mA (0~24678) 4~20mA (0~24678) | 0~20mA (0~24678) 4~20mA (0~24678) |
| Corresponding value | 0 | 0 |
| Corresponding value | 24678 | 24678 |

- In [Local IO Configuration Interface], click [Display Code Values]/ [Display Data] in the upper right corner. When the interface is [Display Code Values], it has been switched to [Display Code Value] status, as shown below.

- In the [IOGVL] window, if the 5# channel and the 6# channel of 4038 output 100 and 65535, respectively, and write them, we can see that the values of the 1# channel and the 3# channel of 3138 will become 75-76 (the code value may fluctuate) and 65535, as shown below.

If entering 0 in the 5# channel and writing it, you can see that the 1# channel will become 0, which is expected.

- Similarly, if the range of 3138 is modified to 0~20mA (0~24678) and the range of 4038 is modified to 0~20mA (0~65535), when 65535 is entered in 4038, 3138 will output 24678, as shown below (when modifying the range, must log out).

Note: The range of input and output modules can only be 0~20mA or 4~20mA at the same time, but not 0~20mA for one module and 4~20mA for the other module.

5. Data display

- The data display means that the displayed IO number is 0~20mA in the running state.

- You can modify the numerical correspondence table under the display status of "Display Data" in "Local IO Configuration Interface".

|  | Src4038 8-channel current output | SRC3138 8-point analog input |
| --- | --- | --- |
| Range | 0~20mA (0~65535) 4~20mA (0~65535) | 0~20mA (0~65535) 4~20mA (0~65535) |
| • | 0~20mA (0~24678) 4~20mA (0~24678) | 0~20mA (0~24678) 4~20mA (0~24678) |
| Corresponding value | 0mA | 0mA |
|  | 4mA | 4mA |
|  | 20mA | 20mA |

- In [Local IO Configuration Interface], click [Display Code Values]/[Display Data] in the upper right corner. When the interface is [Display Data], it has been switched to [Display Data] status, as shown below.

- In the [IOGVL] window, if the 5# channel and the 6# channel of 4038 output 4 and 20 respectively, and write them, we can see that the values of the 1# channel and the 3# channel of 3138 will become 3.9973 ... (with fluctuation) and 20, as shown below.

On the hardware IO module, you can also see that the corresponding indicators have been turned on, as shown below.

(VIII) Pulse module test

1. Pulse module indicator test

1) In this case, two pulse modules, SRC5031 and SRC5001, are used to demonstrate that the hardware IO module indicator is turned on by assigning the number of encoder bits.

2) Connect two pulse modules, SRC5031 and SRC5001, to the iComputer, and add the corresponding IO modules in the metafacture, as shown below.

3) Click [Generate Code] – [Login] – [Start], and the corresponding modules will be green in “Local IO Configuration Interface”, as shown in the right figure above.

4) SRC 5001 pulse module test

- According to the User Manual of SR5111-24V Single-ended Incremental Encoder Counting Module _V1.04.pdf, the indicator function table in this document is shown as follows.

3.2 Indicator functions

| Name | ID | Color | Status | Description |
| --- | --- | --- | --- | --- |
| Encoder input AB-phase indicator | A | Green | ON | The encoder is enabled |
|  | B |  | OFF | The encoder is not enabled |
| Encoder input Z-phase indicator | Z | Green | ON | The encoder Z-phase homing function is enabled |
|  |  |  | OFF | The encoder Z-phase homing function is not enabled |
| Input channel indicator | I0~I2 | Green | ON | The channel has signal input |
|  |  |  | OFF | The channel has no signal input |
| Output channel indicator | O0~O3 | Green | ON | The channel has signal input |
|  |  |  | OFF | The channel has no signal input |

When the encoder is enabled, the encoder input AB-phase indicator will become green; when the encoder Z-phase zero clearing function is enabled, the encoder input Z-phase indicator will become green.

- In [Local IO Configuration Interface], click SRC5001 module – [Channel Basic Parameters] to find the channel name corresponding to [Encoder Count Enable] and [Encoder Z-phase Zero Clear Enable], as shown below.

- In the [IOGVL] interface, set [MO_ 5001 _ 11] and [MO _ 5001 _ 12] to True and write them, as shown below.

- You can see that the indicators of channels A, B and Z on the hardware SRC5001 are turned on, as shown below.

- When the channel value is set to False, the indicator will be turned off.

5) SRC 5031 pulse test

Similarly, if setting the value of the corresponding channel to True, the indicator will be turned on. The specific operation steps are similar to those for SRC5001, please refer to the above description.

2. Connection test of the pulse module and the encoder

1) Encoder count value test

(1) Connection between the encoder and SRC5031

The encoder E6B2-CWZ1X has eight wires, which are connected to the corresponding ports of IO module. The following table shows the terminal names corresponding to the colors of the encoder wires.

| E6B2-CWZ1X |  |
| --- | --- |
| Wire color | Terminal name |
| Brown | Power supply (+VCC) |
| Black | Output A+ phase |
| White | Output B+ phase |
| Orange | Output Z+ phase |
| Black/red with red edge | Output A- phase |
| White/red with red edge | Output B- phase |
| Orange/red with red edge | Output C- phase |
| Blue | 0V |

Connect the above wires with the corresponding ports of IO module, and the following figure shows the correspondence relationship.

Black

White

Orange

Brown

Black/Red

White/Red

Orange/Red

Blue

(2) In the [IOGVL] interface, set the enabling channel "MO_5031_11" of SRC5031 module to True, and turn the encoder to see the change of the value in the "MI_5031_7" channel, as shown below.

2) Encoder comparison channel test

(1) Connect the devices as above.

(2) Set the “encoder compare output channel 1 enable”, “encoder compare output channel 2 enable”, “encoder compare output channel 1 compare direction”, “encoder compare output channel 2 compare direction”, “encoder compare output channel 1 trigger mode” and “encoder compare output channel 2 trigger mode” to True.

(3) Set the “setting value of encoder compare output channel 1” and the “setting value of encoder compare output channel 2” to "3000" and "5000" respectively in the "IOGVL" interface.

(4) Select [Local IO Configuration Interface]- [Pulse Module], and set the “encoder compare output channel 1 pulse time” and “encoder compare output channel 2 pulse time” to 3000 and 5000 respectively.

(5) Click [Generate Code] – [Login] – [Start] to write the above values, as shown below.

(6) Set "MO_5031_11" to True, and turn the encoder to see the change of the value of "MI_5031_7". When the value is greater than 3000, the O0 indicator in SRC5031 module will be turned on for 3000ms (3s); when the value is greater than 5000, the O1 indicator in SRC5031 module will be turned on for 5000ms (5s).

3) Encoder probe mode test

(1) Connect the encoder with the IO module, as shown above.

(2) Set "encoder probe input channel 1 latch enable” MO_5031_24 and "encoder probe input channel 2 latch enable" MO_5031_25 to True.

(3) Turn the encoder to a certain value.

(4) In addition, connect the positive pole to the SRC5031 module I0 (probe) and the negative electrode is connected to the SRC5031 module C1; you will see that the indicator of module I0 is turned on, indicating that the encoder value has been stored in "MI_5031_8", as shown below.

(5) Similarly, connect the positive pole to the SRC5031 module I1 (probe) and the negative electrode to the SRC5031 module C1; you will see that the indicator of module I1 is turned on, indicating that the encoder value has been stored in "MI_5031_9", as shown below.

4) Connection test between SRC5001 and the encoder

(1) Connect wires

Connect the corresponding wires on the encoder to the 5001 module according to the following table.

| E6B2-CWZ5B |  |
| --- | --- |
| Wire color | Terminal name |
| Brown | Power supply (+VCC) |
| Black | Output A phase |
| White | Output B phase |
| Orange | Output C phase |
| Blue | 0V |

(2) As same as the test of 5031, in the [IOGVL] interface, set the enabling channel "MO_5001_11" of SRC5001 module to True, and turn the encoder to see the change of the value in the "MI_5001_7" channel, as shown below.

(3) For the comparison channel test, refer to the test method for 5031.

(4) For the probe channel test, refer to the test method for 5031.

5) Connection test between SRC5041 and the encoder

(1) Connect the wires

Connect the corresponding wires on the encoder to the 5041 module according to the following table.

| ST-5008-13-SS |  |
| --- | --- |
| Wire color | Terminal name |
| Red | +VCC |
| Black | 0V |
| Green | C+ |
| Yellow | C- |
| Brown | D+ |
| Orange | D- |

(2) Turn the encoder continuously, and you can see that the D+, D-, C+ and C- indicators on the module are turned on.